## Sheet1
resolution | Energy Yield (kWh/kWp) | Net Energy (MWh/year) | Performance Ratio (%) | Production DC (kWh) | Production AC (kWh) | GHI (kWh/m^2) | GI (kWh/m^2) | Average Temperature (C) | Inverter Min DC Voltage | Inverter Max AC Power | Inverter Max DC Current | Inverter Max DC Voltage | Inverter Min DC Power | Inverter Efficiency | Inverter Tare
1 | 137.3449 | 54.2238 | 72.22% | 59731.0483 | 54223.7735 | 190.4107 | 190.1809 | 25.0314 | -0.03842% | -3.444% | -2.392% | 0% | 0% | -3.349% | -0.03871%
2 | 137.9166 | 54.4495 | 72.49% | 59797.849 | 54449.4629 | 190.4107 | 190.2506 | 25.0314 | -0.03621% | -3.312% | -2.195% | 0% | 0% | -3.348% | -0.03857%
5 | 138.9559 | 54.8598 | 73% | 59909.5052 | 54859.7703 | 190.4107 | 190.3628 | 25.0314 | -0.03287% | -3.121% | -1.869% | 0% | 0% | -3.343% | -0.03828%
10 | 140.0783 | 55.3029 | 73.55% | 60013.2205 | 55302.914 | 190.4107 | 190.459 | 25.0314 | -0.03035% | -2.875% | -1.541% | 0% | 0% | -3.343% | -0.03789%
15 | 140.8492 | 55.6073 | 73.92% | 60070.5965 | 55607.2533 | 190.4107 | 190.537 | 25.0314 | -0.03053% | -2.699% | -1.389% | 0% | 0% | -3.344% | -0.03764%
20 | 140.9824 | 55.6598 | 74% | 60091.0242 | 55659.8427 | 190.4107 | 190.5248 | 25.0314 | -0.02982% | -2.68% | -1.315% | 0% | 0% | -3.339% | -0.0377%
30 | 141.9043 | 56.0238 | 74.47% | 60159.1837 | 56023.8069 | 190.4107 | 190.5552 | 25.0314 | -0.03185% | -2.545% | -1.071% | 0% | 0% | -3.342% | -0.037%
60 | 142.4874 | 56.254 | 74.77% | 60180.3505 | 56254.0262 | 190.4107 | 190.5702 | 25.0314 | -0.03201% | -2.361% | -0.8923% | 0% | 0% | -3.336% | -0.03619%
120 | 141.8796 | 56.0141 | 74.55% | 60261.9662 | 56014.0507 | 190.4107 | 190.3103 | 25.0314 | -0.07159% | -2.109% | -0.7157% | 0% | 0% | -3.372% | -0.03037%

## Sheet2
average or instant | resolution (minutes) | Energy Yield (kWh/kWp) | Net Energy (MWh/year) | Performance Ratio (%) | Production DC (kWh) | Production AC (kWh) | GHI (kWh/m^2) | GI (kWh/m^2) | Inverter Min DC Voltage | Inverter Max AC Power | Inverter Max DC Current | Inverter Max DC Voltage | Inverter Min DC Power | Inverter Efficiency | Inverter Tare
average | 1 | 137.6374 | 54.3392 | 72.3758 | 59693.4706 | 54339.2234 | 190.4107 | 190.1705 | -0.03433% | -3.425% | -2.27% | 0% | 0% | -3.482% | -0.03863%
average | 5 | 139.2695 | 54.9836 | 73.1639 | 59871.9674 | 54983.581 | 190.4107 | 190.3527 | -0.02999% | -3.093% | -1.767% | 0% | 0% | -3.464% | -0.03817%
average | 15 | 140.9418 | 55.6438 | 73.9746 | 60033.1123 | 55643.8398 | 190.4107 | 190.5274 | -0.02854% | -2.666% | -1.308% | 0% | 0% | -3.447% | -0.03764%
average | 30 | 141.8332 | 55.9958 | 74.4352 | 60121.8184 | 55995.7511 | 190.4107 | 190.5458 | -0.02988% | -2.501% | -1.006% | 0% | 0% | -3.438% | -0.03714%
average | 60 | 142.4132 | 56.2247 | 74.7344 | 60142.348 | 56224.7289 | 190.4107 | 190.559 | -0.03026% | -2.323% | -0.8299% | 0% | 0% | -3.425% | -0.03657%
instant | 1 | 137.6374 | 54.3392 | 72.3758 | 59693.4706 | 54339.2234 | 190.4107 | 190.1705 | -0.03433% | -3.425% | -2.27% | 0% | 0% | -3.482% | -0.03863%
instant | 5 | 137.8319 | 54.416 | 72.2451 | 59872.4474 | 54416.0274 | 190.9867 | 190.7837 | -0.03505% | -3.495% | -2.348% | 0% | 0% | -3.486% | -0.0386%
instant | 15 | 138.0804 | 54.5141 | 72.1477 | 60034.2565 | 54514.1088 | 191.5456 | 191.3857 | -0.03668% | -3.542% | -2.378% | 0% | 0% | -3.495% | -0.03842%
instant | 30 | 136.7102 | 53.9732 | 72.3016 | 59357.1604 | 53973.1813 | 189.4294 | 189.0833 | -0.03674% | -3.485% | -2.32% | 0% | 0% | -3.477% | -0.03859%
instant | 60 | 138.401 | 54.6407 | 72.379 | 60033.7547 | 54640.7052 | 191.681 | 191.217 | -0.02745% | -3.417% | -2.303% | 0% | 0% | -3.478% | -0.03849%
inst60avg | 1 | 142.4132 | 56.2247 | 74.7344 | 60142.348 | 56224.7289 | 190.4107 | 190.559 | -0.03026% | -2.323% | -0.8299% | 0% | 0% | -3.425% | -0.03657%
inst60avg | 5 | 142.1104 | 56.1052 | 74.3441 | 60294.0692 | 56105.1801 | 190.9867 | 191.1521 | -0.03055% | -2.585% | -1.016% | 0% | 0% | -3.433% | -0.03665%
inst60avg | 15 | 142.0193 | 56.0692 | 74.0614 | 60443.8588 | 56069.2348 | 191.5456 | 191.7589 | -0.03058% | -2.626% | -1.283% | 0% | 0% | -3.434% | -0.03655%
inst60avg | 30 | 138.8489 | 54.8175 | 73.3501 | 59573.0017 | 54817.5431 | 189.4294 | 189.2961 | -0.0301% | -2.97% | -1.726% | 0% | 0% | -3.435% | -0.03751%
inst60avg | 60 | 138.401 | 54.6407 | 72.379 | 60033.7547 | 54640.7052 | 191.681 | 191.217 | -0.02745% | -3.417% | -2.303% | 0% | 0% | -3.478% | -0.03849%
| Expected Yield | Expected Clipping Loss
0 | 137.6374 | -3.425%
60 | 137.6374 | -3.425%
underpredicted clipping loss